## plant_design
STP Design Data — legacy paper surveys digitised 2018–2023
source: onboarding team paper survey forms, transcribed by domain team
Plant ID | Client Name | Sector | Plant Location | Start of operation | Design Flow (KLD) | Mean flow, kld | Peak Flow KLD | Peak flow timing | Unit processes | PFD displayed?
P-25 | Trident Grove Residency | Residential building | Basement | 2016-08 | 400 | 310 kld avg | 2883 | 6:30-8:30, 18:30-20:30 | MBBR, Clarification, Media filtration, Chlorination | Yes
P-26 | Nandini Foods & Snacks | Industrial effluent plant | Ground level | Apr 2021 | 300 | 230 | 596 | 6-8am & 7-9pm | OGT; EQ; MBBR; Tube settling; UV | yes
P-27 | Emerald Bay Offices | Commercial - office | Ground level | 2016 | 700 | 570 | 1396 | 0700-0900 / 1800-2000 | EQ + ASP + Clarification + MF | no
P-28 | Shakti Steel Rolling | industrial | Ground level | 2016-08 | 950 | 770 | 2125 | morning only 6-9 | Equalization, Anoxic, MBBR, Clarification, Chlorination | No
P-29 | Cedarwood Villas | Residential building | Basement |  | 300 | 250 | 580 | 6-8am & 7-9pm | OGT; EQ; MBBR; Tube settling; UV | no
P-30 | Anandpur Municipal STP | Municipal | Basement | Dec 2016 | 950 | 770 | 1940 | single peak 7-10am | Screening; Equalization; SBR; MF; Chlorination | FALSE

## water quality
Water quality — as reported by onboarding team
single grab samples unless noted; some plants had no lab report on site
Plant ID | Client Name | Inlet COD (mg/L) | Inlet BOD (mg/L) | Inlet Total N (mg/L) | Inlet TSS (mg/L) | Inlet pH | Outlet COD (mg/L) | Outlet BOD (mg/L) | Outlet Total N (mg/L) | Outlet TSS (mg/L) | Outlet colour | Objectionable odour at outlet? | Outlet photo ref
P-25 | Trident Grove Residency | 800 |  | 75 | 377 | 6.7 | 53 | 18 | 1.5 |  | Yellowish | N | IMG_4129.jpg
P-26 | Nandini Foods & Snacks | 473 | 217 | 56 | 435 | 7.6 | 46 | 6 | 3.8 | 12 | Clear/colourless | N | IMG_2343.jpg
P-27 | Emerald Bay Offices | 555 | 325 | 48 | 425 | 6.9* | 43 | 13 | 8.1 | 15 | Light brown | No | IMG_2858.jpg
P-28 | Shakti Steel Rolling | 1060 | 353 | 89 | 205 | 7.8 | 32 | 19 | 10 | 17 | Slightly turbid | no | IMG_1343.jpg
P-29 | Cedarwood Villas | 445 | 340 | 82 | 422 | 6.9 | 69 | 16 | 8.4 | 28 | Slightly turbid | No | IMG_1131.jpg
P-30 | Anandpur Municipal STP | 451 | 213 | 80 | 156 | 8.2 | 68 | 8 | 9.1 | 16 | Pale yellow | no | IMG_4323.jpg

## water_balance
Compiled by domain team — please do not edit, ask before changing values
Plant ID | Client Name | Freshwater source | Freshwater cost (Rs/KL) | Domestic consumption (KL/day) | Laundry consumption (KL/day) | Kitchen consumption (KL/day) | Freshwater TDS (mg/L) | Freshwater pH | Freshwater hardness (mg/L as CaCO3) | Freshwater fluoride (mg/L) | Wastewater source | Treated water destination | Reuse fraction | Reuse - flushing (KL/day) | Reuse - gardening (KL/day) | Reuse - cooling tower (KL/day) | Reuse point TDS (mg/L) | Water balance displayed?
P-25 | Trident Grove Residency | Municipal + Borewell | 47 | 310 | 10 | 170 | 116 | 7.1 | 61 | 0.17 | Domestic sewage | On-site reuse; Sewer discharge | 0.7 | 130 | 60 | 0 | 1000 | Y
P-26 | Nandini Foods & Snacks | Tankers | 56 | 170 KLD | 15 | 30 | 216 | 7.8 | 128 | 0.1 | Domestic sewage | Surface water discharge | 76% | 180 | 20 | 0 | 877 | Y
P-27 | Emerald Bay Offices | Surface | 53 | 400 | 80 | 165 | 83 |  | 138 | 0.25 | Domestic sewage; Kitchen/canteen | On-site reuse | 0.26 | 70 | 65 | 0 | 502 | no
P-28 | Shakti Steel Rolling | Municipal / tankers | 60 | 570 | 40 | 70 | 198 | 8.1 | 68 | 0.02 | Industrial effluent, Wash water | Surface water discharge | 0.85 | 90 | 60 | 0 | 747 | N
P-29 | Cedarwood Villas | Surface | INR 43 | 220 | 75 | 195 | 110 | 6.9 | 175 | 0.1 | Municipal sewage | On-site reuse, Groundwater recharge | 0.29 | 100 | 15 | 120 | 522 | yes
P-30 | Anandpur Municipal STP | Borewell | 50 | 780 | 80 | 100 | 850 | 8.1 | 55 | 0.04 | Industrial effluent, Wash water | Zero liquid discharge (ZLD) | 0.57 | 140 | 75 | 200 | 945 | FALSE

## site-characteristics
Site characteristics — collection tank
revised after second site visit, see email thread 14 Feb
'Plant Location' re-recorded here because the design sheet was filled in from drawings, not from the site
| Plant_ID | Client Name | Plant Location | Tank material of construction | Open / covered / sealed | Tank condition | Tank accessibility | Cable run to panel (m) | Sludge visible in tank?
| P-25 | Trident Grove Residency | Basement | RCC (lined) | open | Good | Easy | 24 | Yes
| P-26 | Nandini Foods & Snacks | Ground level | FRP | Open |  | Restricted | 7 | Yes
| P-27 | Emerald Bay Offices | Ground level | FRP | Sealed/Closed | Poor | Restricted | 29 | TRUE
| P-28 | Shakti Steel Rolling | Ground level | RCC | covered | Fair | Restricted | 11 | N
| P-29 | Cedarwood Villas | Ground level | MS | Open | Fair | Unsafe | 23 | TRUE
| P-30 | Anandpur Municipal STP | Basement | MS with epoxy lining | open | Fair | Easy | 28 | yes

## process_design
Process design — collection tank sizing
collection tank only; other unit processes are in the technology workbooks
no plant code recorded on these forms
Client Name | Tank count | Tank arrangement (rows x cols) | Tank shape | Tank volume (m3) | Tank length (m) | Tank width (m) | Tank diameter (m) | Tank height (m) | Same dimensions for all tanks? | Sludge wasting (per day)
Trident Grove Residency | 1 | 1 x 1 | Rectangular | 9 | 2.4 | 1.5 |  | 2.5 |  | 2
Nandini Foods & Snacks | 2 | 1 x 1 | Rectangular | 5.46 | 2.1 | 1.3 |  | 2 |  | 3
Emerald Bay Offices | 2 | 2 x 1 | Rectangular | 0.56 | 0.9 | 0.62 |  | 1 |  | 2
Shakti Steel Rolling | 1 | 1 x 1 | Cylindrical | 29.86 m3 |  |  | 3.9 | 2.5 |  | 1/2
Cedarwood Villas | 1 | 1 x 1 | Rectangular | 13.54 | 2 | 1.2 |  | 3 |  | 1
Anandpur Municipal STP | 1 | 1 x 1 | Rectangular | 31 | 5 | 3.1 |  | 2 |  | 1